## PJM Cycle 1 Checklist
PJM Cycle 1 Application Checklist — Zonevex
Application Deadline: April 27, 2026 ¦ Generated by zonevex.com
Category | Item # | Requirement | Description | How to Complete | Status | Due Date | Risk Level | OATT/Manual Reference | Cure Difficulty if Deficient
Entity & Legal | 1 | Legal Entity Formation | Entity must be fully formed and in good standing in its state of organization | Verify state registration is current; obtain Certificate of Good Standing from Secretary of State | Not Started |  | High | Manual 14H | Low — file reinstatement
Entity & Legal | 2 | Entity Name Consistency | Legal entity name on application must EXACTLY match all site control documents, financial instruments, and certifications — including punctuation, abbreviations, and legal suffixes (LLC vs L.L.C.) | Create entity name matrix: list every document and verify name matches. Use Template C (Site Control Summary) and Template D (QA Signoff). If mismatch found: amend document or execute assignment agreement BEFORE submission. | Not Started |  | Critical | Manual 14H §2 | Moderate — requires counterparty cooperation
Entity & Legal | 3 | Authorized Signatory Designated | Officer or authorized representative identified with actual corporate authority to sign certifications and ASA | Prepare corporate resolution or authorization document granting signing authority. Keep on file for potential PJM challenge. | Not Started |  | Medium | Manual 14H | Low — internal document
Entity & Legal | 4 | No Outstanding PJM Debts | Confirm entity (and any affiliated entities) has no unpaid balances from prior interconnection requests | Contact InterconnectionSupport@pjm.com to confirm clean payment history. If debts exist: pay in full before submission. | Not Started |  | High | OATT Part IV | Low — pay outstanding balance
Entity & Legal | 5 | Corporate Authorization Document | Resolution or authorization from managing member/board authorizing the interconnection application and designating signatory | Draft board resolution or managing member consent authorizing: (1) application submission, (2) deposit commitments, (3) designated signatory. Have executed copy ready. | Not Started |  | Medium | Manual 14H | Low — internal document
Site Control | 6 | 100% Site Control — Generating Facility | Must demonstrate full site control for entire generating facility footprint at time of application | Assemble all deeds, leases, options, or development agreements covering the project site. Verify coverage includes: generating equipment area, access roads, laydown/staging areas, setback zones, stormwater management areas. | Not Started |  | Critical | OATT Part VII §302 | High — 10 days insufficient for new agreements
Site Control | 7 | Site Control Documents in Entity Name | ALL site control evidence must be in the EXACT same legal entity name as the applicant on the PJM application | Cross-reference every site control document against application entity name. If mismatch: execute assignment agreement with complete chain of title documentation, or amend the document with counterparty. | Not Started |  | Critical | OATT Part VII §302 | Moderate — depends on counterparty
Site Control | 8 | Site Control Term >= 1 Year | Evidence must show control through at least April 27, 2027 (1 year from application deadline) | Check expiration date on every site control document. If any expire before April 27, 2027: negotiate and execute term extension amendment with landowner. Build auto-renewal provisions into future agreements. | Not Started |  | Critical | FERC Order 2023 | Moderate — requires landowner amendment
Site Control | 9 | Acceptable Form of Site Control | Must be: deed (ownership), executed lease, development agreement, option to purchase/lease, or other sufficient documentation | Verify each document is one of the accepted forms per §302. Unexercised options must be currently exercisable (not expired or contingent). LOIs and verbal agreements are NOT acceptable. | Not Started |  | High | OATT Part VII §302 | High — requires new agreement execution
Site Control | 10 | Full Project Footprint Coverage | Site control must cover ALL land needed: generating equipment, access roads, construction laydown areas, setback zones, stormwater areas | Commission boundary survey overlaid with Attachment N site plan. Every square foot shown on site plan must fall within controlled parcels. Common gaps: access roads crossing third-party land, setbacks extending beyond parcel boundary. | Not Started |  | Critical | Manual 14G Attachment N | High — acquiring additional land in 10 days is extremely difficult
Site Control | 11 | Solar: Land Adequacy Engineering Analysis | For solar: engineering analysis demonstrating sufficient controlled acreage for proposed MW capacity | Calculate: (Panel wattage x panel count) = nameplate MW. Calculate required acreage using GCR and row spacing. Compare to controlled acreage. Document panel type, arrangement (fixed/tracker), GCR, inter-row dimensions. | Not Started |  | High | Manual 14H | Moderate — may require MW reduction or engineering revision
Site Control | 12 | Interconnection Facility Route Assessment | Identify likely gen-tie route from facility to POI; begin securing site control for 50% requirement at DP1 | Map probable gen-tie routes using GIS + parcel data. Identify landowners along each route. Secure options on parcels along 2-3 likely routes (path may change after Phase I). Budget for easement acquisition. | Not Started |  | Medium | OATT Part VII §302 | N/A — not required at application but critical for DP1
Technical | 13 | Site Plan — Attachment N | Detailed site plan showing: equipment layout with dimensions, property boundaries, POI location, gen-tie route, access roads, setbacks, scale, north arrow, coordinate reference | Engage surveyor/engineer to prepare. Must show ALL elements (see Playbook Section 3.3). For solar: overlay panel arrangement on parcel boundaries. Ensure MW implied by layout matches application MW exactly. | Not Started |  | Critical | Manual 14G Attachment N | Moderate — requires engineering revision
Technical | 14 | System Impact Study Data Form (B-1) | Attachment B-1: Generating facility technical data — nameplate (MW/MVA), power factor, voltage, transformer specs, reactive capability, governor/exciter parameters | Complete every field using equipment manufacturer datasheets. Verify nameplate MW matches application and site plan. For solar: include inverter-level data. Have EPC or electrical engineer review for completeness. | Not Started |  | High | Manual 14G Attachment B-1 | Moderate — requires engineering input
Technical | 15 | Dynamic Model Data (B-2) | Attachment B-2: PSSE-compatible dynamic model file (.dyr) for PSSE v33+, with manufacturer documentation | Request PSSE model from equipment manufacturer NOW — lead time is 4-8 weeks. For solar: need REGC_A/REEC_A/REPC_A parameters. For storage: state-of-charge model. Parameters must match B-1 data. | Not Started |  | High | Manual 14G Attachment B-2 | High — manufacturer lead times are weeks/months
Technical | 16 | MW Consistency Across All Documents | Nameplate capacity (MW) must be identical on: application, site plan, engineering analysis, site control acreage calculation, technical data forms | Create MW cross-reference table. Check: application form, Attachment N site plan, solar engineering analysis, B-1 data form. Even small discrepancies trigger deficiency. | Not Started |  | Critical | Manual 14H | Low — correct the inconsistent document
Technical | 17 | Point of Interconnection (POI) Identified | Specific substation or transmission line identified by exact PJM facility name AND voltage level | Identify specific facility (e.g., 'XYZ Substation 138 kV bus'). Verify name against PJM queue spreadsheet naming conventions. Verify facility exists and is operational. Contact InterconnectionSupport@pjm.com to pre-validate. | Not Started |  | High | Manual 14G | Low — resubmit with corrected POI
Technical | 18 | One-Line Diagram | Electrical one-line showing facility interconnection configuration from generator terminals through step-up transformer to POI | Engage electrical engineer. Must show: generators/inverters, collector system, step-up transformer(s), gen-tie, metering, protective relaying, POI connection. Must match equipment specs and site plan. | Not Started |  | Medium | Manual 14G | Moderate — requires engineering
Technical | 19 | Equipment Specifications | Manufacturer, model, nameplate ratings for all primary generating equipment | Compile datasheets for: panels/turbines, inverters, transformers, BESS modules (if applicable). Include fault current contribution data for inverters. | Not Started |  | Medium | Manual 14G | Low — request from vendor
Technical | 20 | Storage: Operating Assumptions | Charging source, duration (hours), dispatch profile, round-trip efficiency, degradation, state-of-charge management | Document comprehensively. FERC rejected PJM's initial storage assumptions (July 2025). Verify current requirements against October 2025 compliance filing (Docket ER24-2045). Contact PJM for latest guidance. | Not Started |  | High | FERC Order 2023-A / ER24-2045 | Moderate — requires technical documentation
Technical | 21 | Hybrid: Component Interaction | How generation and storage components interact operationally — shared vs independent inverters, dispatch coordination, single vs multiple resource registration | Write 2-3 page operational concept document covering: charging source, dispatch logic, inverter configuration, PJM market registration approach. | Not Started |  | Medium | Manual 14H | Moderate — requires technical documentation
Financial | 22 | Study Deposit Calculated | Calculate study deposit based on project capacity tier: $75K (0-20MW) to $400K (>750MW) | Use PJM Deposit Calculator: pjm.com/planning/service-requests/application-and-forms/deposit-calc. Use the GREATER of energy value or capacity value for MW. Have second person verify calculation. | Not Started |  | Critical | Manual 14H §6 | Low — fund correct amount
Financial | 23 | Study Deposit Funded | Cash, irrevocable letter of credit (ILOC), or surety bond in correct amount ready for submission | Arrange funding in acceptable form. If using ILOC or surety bond: verify PJM accepts the issuing institution. Allow lead time for ILOC issuance (1-2 weeks typical). | Not Started |  | Critical | Manual 14H §6 | Low — fund correct amount
Financial | 24 | Readiness Deposit No. 1 Calculated | RD1 = $4,000 x MW (using greater of energy or capacity value) | Calculate: $4,000 x [project MW]. Example: 100 MW = $400,000. Verify MW figure matches application. | Not Started |  | Critical | Manual 14H §6 | Low — fund correct amount
Financial | 25 | Readiness Deposit No. 1 Funded | Payment form confirmed and submitted with application | Same acceptable forms as study deposit: cash, ILOC, or surety bond. | Not Started |  | Critical | Manual 14H §6 | Low — fund correct amount
Financial | 26 | Future Deposit Obligations Budgeted | RD2 (10% of upgrade costs minus RD1) and RD3 (20% minus total RDs) — model under low/medium/high scenarios | Run Financial Calculator with three scenarios: $240/kW (favorable), $400/kW (moderate), $600/kW (congested). Ensure capital reserves or committed financing covers worst case. You'll have 30 days to fund RD2/RD3 after study results. | Not Started |  | High | Manual 14H §6.2 | N/A — planning item
Financial | 27 | Withdrawal Penalty Exposure Calculated | Maximum penalty = 9x study deposit. Know your exposure before committing. | Calculate: study deposit x 9 = max penalty. Example: $250K deposit = $2.25M max penalty. Understand exemption conditions (>25% cost increase, 100% individual increase, no material impact). | Not Started |  | High | Manual 14H §6.2.1 | N/A — planning item
Financial | 28 | Application Fee | $5,000 standard PJM application fee | Include with submission payment. | Not Started |  | Low | Manual 14H | Low — pay fee
Agreements | 29 | Application and Studies Agreement (ASA) | Fully executed ASA signed by authorized representative — current Cycle 1 version | Download current ASA from PJM portal (NOT transition cycle version). Review key provisions: study cost obligations, withdrawal penalty consent, cluster methodology consent. Have legal counsel review. Execute and include with application. | Not Started |  | Critical | OATT Part VII Subpart A | Low — execute correct version
Agreements | 30 | Cycle Application Officer Certification | Signed by officer or authorized representative — current PJM Cycle 1 form | Download current form from PJM portal. Signatory must be the person identified in corporate authorization document. Sign and include with application. | Not Started |  | Critical | Manual 14H | Low — sign correct form
Agreements | 31 | PJM OATT Part VII Review Completed | Understand tariff provisions governing your interconnection rights and obligations | Read OATT Part VII, Subpart A (general provisions), Subpart D (study procedures), §302 (site control), §307-310 (study phases), §314 (GIA negotiation). Focus on provisions governing your technology type. | Not Started |  | Medium | OATT Part VII | N/A — knowledge item
Agreements | 32 | Consent-to-Assignment Forms (if applicable) | Required if project rights will be assigned during or after study process | Download appropriate version: Combined Buyer-Seller, Seller-only, or Buyer-only. Only needed if assignment is planned — keep on file. | Not Started |  | Low | Manual 14H | Low — administrative
Permitting | 33 | Permitting Pathway Documented | List of all required permits (federal, state, local) with issuing authority, status, and timeline | Create permit matrix: permit name, issuing authority, application status, expected timeline, known risks. See Playbook Section 10 for state-specific requirements. Include even if no applications filed yet. | Not Started |  | High | Manual 14H | N/A — documentation item
Permitting | 34 | Local/County Permits Identified | Conditional use, special exception, building permits — requirements identified per project jurisdiction | Research local zoning ordinance for project site. PA: township conditional use. OH: county + OPSB if >=50MW. Contact local planning office for current requirements. | Not Started |  | Medium | State-specific | N/A — external process
Permitting | 35 | State-Level Permits Identified | Environmental, utility commission, or siting board approvals required by state | PA: Chapter 102/105 via DEP. NJ: BPU + NJDEP. VA: DEQ PBR (<=150MW) or SCC CPCN. MD: PSC CPCN (>2MW). OH: OPSB (>=50MW). See Playbook Section 10 for full details. | Not Started |  | Medium | State-specific | N/A — external process
Permitting | 36 | Environmental Studies Initiated | Wetlands delineation, threatened/endangered species survey, cultural resources, noise study, Phase I ESA | Engage environmental consultant. VA PBR requires 12-month wildlife monitoring — start immediately if not yet begun. Timeline: 3-12 months depending on scope. | Not Started |  | Medium | State-specific | N/A — external process
Permitting | 37 | Community Engagement Documented | Evidence of landowner engagement, community notification, public meeting participation | Document all community interactions. OH requires 2 public information meetings. MD requires notification to officials within 1 mile. Keep records of all outreach and responses. | Not Started |  | Low | State-specific | N/A — external process
Quality Assurance | 38 | Entity Name Verification Matrix | Every document cross-checked against application entity name — using Template C | Create table listing every document with the entity name exactly as it appears. Flag any discrepancy. Fix ALL mismatches before submission. | Not Started |  | Critical | N/A | N/A — pre-submission QA
Quality Assurance | 39 | MW Consistency Cross-Reference | All MW figures verified across application, site plan, engineering analysis, technical data forms, site control acreage | Create MW cross-reference: application [__MW], site plan [__MW], B-1 form [__MW], solar engineering [__MW], acreage calc [__MW]. All must match exactly. | Not Started |  | Critical | N/A | Low — correct inconsistent document
Quality Assurance | 40 | POI Specificity Verification | POI identifies exact substation or transmission line by PJM facility name and voltage | Cross-reference POI name against: PJM queue spreadsheet, PJM transmission maps, Queue Scope tool. Confirm exact naming convention PJM uses. | Not Started |  | High | N/A | Low — resubmit corrected POI
Quality Assurance | 41 | Current PJM Forms Verification | All forms downloaded fresh from PJM portal — Cycle 1 versions, not Transition Cycle | Download ALL forms in the week before submission. Create document index listing: form name, version/revision number, download date. Do NOT reuse prior-cycle forms. | Not Started |  | High | N/A | Low — download correct forms
Quality Assurance | 42 | Site Control Expiration Audit | All site control documents verified to expire AFTER April 27, 2027 | List every site control document with expiration date. Flag any expiring before April 27, 2027. Execute extensions BEFORE submission. | Not Started |  | Critical | FERC Order 2023 | Moderate — requires landowner amendment
Quality Assurance | 43 | Deposit Amount Verification | Study deposit and RD1 verified via PJM official Deposit Calculator | Run calculator at pjm.com/planning/service-requests/application-and-forms/deposit-calc. Screenshot result. Have second person verify independently. | Not Started |  | Critical | Manual 14H §6 | Low — correct the amount
Quality Assurance | 44 | Legal Review of Complete Package | Entire submission package reviewed by qualified energy/interconnection attorney | Engage attorney with PJM interconnection experience. Review: ASA terms, site control sufficiency, entity consistency, deficiency risk areas. Budget $5-15K for review. | Not Started |  | High | N/A | N/A — pre-submission QA
Quality Assurance | 45 | Backup Copy of Entire Package | Complete copy of every submitted document stored separately from NextGen | Save complete package to: (1) cloud storage, (2) local drive. Essential for reference during 10-day deficiency cure window. Include all uploaded documents, forms, and payment confirmations. | Not Started |  | Medium | N/A | N/A — administrative
Quality Assurance | 46 | Document Index Created | Master list of every document in submission: filename, description, version, date | Create spreadsheet listing every file uploaded to NextGen with: document name, category, date prepared, preparer, PJM requirement it satisfies. | Not Started |  | Medium | N/A | N/A — administrative
Quality Assurance | 47 | NextGen Account Verified | Account active with Read/Write access; Company Profile completed | Log into NextGen and verify: (1) account is active, (2) you have Read/Write role, (3) Company Profile is complete. Non-members: contact Account Manager for CAM assignment — allow business days. | Not Started |  | High | N/A | N/A — do this NOW
Quality Assurance | 48 | Pre-Submission QA Signoff | Complete Template D (QA Signoff) with all 15 verification checks signed off by preparer, reviewer, and approver | Use Template D from Playbook Section 13. Do not submit until all 15 checks are verified and signed. If any check fails: resolve before submission. | Not Started |  | Critical | N/A | N/A — pre-submission QA
Quality Assurance | 49 | Submit Before Deadline Day | Application submitted via NextGen BEFORE April 27, 2026 — do not wait until deadline day | Technical issues, upload failures, or payment processing delays on deadline day can cause missed submission. Submit 2-3 business days early. | Not Started |  | Critical | Manual 14H | N/A — timing discipline