## POI Evaluation
PJM Cycle 1 Point of Interconnection (POI) Evaluation — Zonevex
Evaluate candidate substations and transmission lines for your interconnection request
Section | Field | Value | How to Find This Data | Source URL / Tool
| POI Candidate #1 Name |  | Enter exact PJM facility name (e.g., 'Smith Substation 138 kV')
POI Candidate #2 Name
| POI Candidate #3 Name |  |  | Evaluate 2-3 candidates before committing
---
Thermal Analysis
| Thermal headroom available? |  | Run Queue Scope at this POI bus | https://queuescope.pjm.com/queuescope/pages/public/evaluator.jsf
| Congestion severity (Queue Scope) |  | Green = low / Yellow = moderate / Red = high | Queue Scope heat map
| Loading impact rating |  | % facility loading impact shown in Queue Scope | Queue Scope
---
Transfer Capability
| ATC at this corridor (MW) |  | Look up Available Transfer Capability | http://oasis.pjm.com
| TTC at this corridor (MW) |  | Total Transfer Capability | http://oasis.pjm.com
| Is ATC > 0? |  | If ATC = 0: this corridor is congested. Expect expensive upgrades. | PJM OASIS
---
Queue Density
| # of active projects at this POI |  | Count projects targeting same substation/line | https://www.interconnection.fyi/?market=PJM
| Total MW queued at this POI |  | Sum of all active project capacities at this POI | Interconnection.fyi or PJM queue download
| # of projects withdrawn from this POI (last 2 years) |  | High withdrawals = potential cost issues | PJM queue data
---
Historical Cost Data
| Avg upgrade cost from recent studies at this POI ($/kW) |  | Review Phase I/II reports from Transition Cycle projects at this POI | PJM study reports (request via InterconnectionSupport@pjm.com)
| Were any projects terminated at this POI in Transition Cycle? |  | Check PJM queue data for TC1 withdrawals at this location | PJM queue data
---
Gen-Tie Assessment
| Distance from project site to POI (miles) |  | Measure via GIS; gen-ties >10 miles = high cost + site control risk | GIS / Google Earth
| # of landowner parcels along probable route |  | Count parcels the gen-tie would cross | County parcel data / GIS
| Is route along existing road ROW or transmission corridor? |  | Existing ROW is easier/cheaper to secure | County GIS / aerial imagery
| Any known obstacles (rivers/highways/rail/federal land)? |  | These can make a route infeasible or very expensive | GIS / aerial imagery
| Estimated gen-tie cost (rough) |  | Rule of thumb: $1-3M per mile for 138kV; higher for 230kV+ | Industry estimates
---
Transmission Owner
| Which TO owns facilities at this POI? |  | Different TOs have different standards, timelines, and responsiveness | PJM TO directory
| TO reputation for study timeliness? |  | Some TOs are known for delays; ask interconnection consultants | Industry knowledge
---
Voltage & Stability (Advanced)
| Known voltage issues in this area? |  | Queue Scope does NOT show voltage — check PJM planning studies | PJM RTEP / planning studies
| Short-circuit concerns? |  | High existing fault current at POI may limit new generation | PJM study reports
| Is POI near stability-limited interface? |  | Stability limits may cap generation regardless of thermal capacity | PJM RTEP
---
POI #1 Summary
| Overall Assessment |  | Green (favorable) / Yellow (proceed with caution) / Red (avoid)
| Estimated upgrade cost range ($/kW) |  | Based on all factors above; compare to $240/kW (active avg) and $599/kW (withdrawn avg)
| Key risks |  |  | List top 2-3 risks
| Recommendation |  | Submit / Evaluate further / Reject
---
| (Repeat all fields above for Candidate #2) |  |  | Copy structure from Candidate #1
---
| (Repeat all fields above for Candidate #3) |  |  | Copy structure from Candidate #1
---
| Factor | Candidate #1 | Candidate #2 | Candidate #3
Thermal headroom
ATC available
Queue density (# projects)
Historical upgrade costs ($/kW)
Gen-tie distance (miles)
Gen-tie parcels to cross
Known voltage/stability issues
TO responsiveness
Overall rating
| RECOMMENDED POI: |  |  | Select the candidate with lowest risk profile
---
| Queue Scope (thermal screening) |  | Free PJM tool — thermal constraints only | https://queuescope.pjm.com/queuescope/pages/public/evaluator.jsf
| Queue Scope User Guide |  |  | https://www.pjm.com/-/media/DotCom/etools/planning-center/queue-scope-user-guide.pdf
| PJM OASIS (ATC data) |  | Updated hourly; transfer capability by corridor | http://oasis.pjm.com
| OASIS User Guide |  |  | https://www.pjm.com/-/media/DotCom/etools/oasis/oasis-user-guide.pdf
| ATC Implementation Document |  |  | https://www.pjm.com/pjmfiles/pub/oasis/ATCID.pdf
| Interconnection.fyi (queue intelligence) |  | Third-party; 1,426 projects, 145.1 GW tracked, daily updates | https://www.interconnection.fyi/?market=PJM
| PJM Official Queue Data |  | Complete queue spreadsheet download | https://www.pjm.com/planning/service-requests
| PJM Interconnection Support |  |  | InterconnectionSupport@pjm.com